| Application |  |  |  |  |
| --- | --- | --- | --- | --- |
| Used as fixed or flexible installed control cable for high voltage (dc) supply for electrical equipments and control units in research. For indoor and outdoor use in dry and wet locations. With reduced smoke emission, corrosiveness and toxicity of combustion gases acc. to CERN safety instruction IS 23. |  |  |  |  |
| Construction |  |  |  |  |
| - Cores - Conductor Tinned copper, flexible stranded, AWG26/7 - Insulation Polyethylene - Colour Code Natural-coloured - Further Construction - Wrapping Min. 1 layer of plastic tape, nom. 36µm - Screen Tinned copper wire braid, opt. coverage min. 80 % - over tinned copper drain wire, AWG26/7 - Outer Sheath Zero halogen, flame retardant polymer - Colour Red - Cable Marking Imprint KERPENWERK CMS EMU CSC HV-CABLE SL-V2YCEH SIZE 6kV(DC) ZERO HALOGEN yy W ww Length marking Manufacturer’s identification thread |  |  |  |  |
| Technical Data |  |  |  | Abbreviations |
| Flame retardancy: IEC 60332-1 Flame propagation: IEC 60332-3-24 cat. C Smoke density: IEC 61034-1 and -2 Amount of halogen acid gas: IEC 60754-1; 0% Degree of acidity of gases: IEC 60754-2 Outer sheath: Limiting Oxygen Index (LOI): min. 43% (IEC 60332-3 ann. B) Temperature Index (TI): min. 260°C (ASTM-D-2863) |  | Temperature range: -30°C up to +70°C (during operation) -5°C up to +50°C (during installation) Min. bending radius: 6 x cable- (fixed installation) 10 x cable- (flexible installation) |  | SL- high voltage cable v tinned copper conductor 2Y insulation of PE C screen of copper wire braid E drain wire H outer sheath of LSZH |
| Test voltage |  |  |  |  |
|  | Character |  | Unit | Values |
| Core / Core | nom. |  | kV (DC) | 12 |
| Core / Screen | nom. |  | kV (DC) | 12 |

| Geometrical and Electrical Data |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Number of | Conductor |  | Core | Cable |  |  |  | Kerpen Part No. |
| Cores | Single-wire- | Conductor resistance at 20°C | Core- | Screen-wire- | Sheath-thickness | Overall Diameter | Weight |  |
|  | (nom.) | (max.) | (approx.) | (nom.) | (nom.) | (approx.) | (approx.) |  |
|  | mm | /km | mm | mm | mm | mm | kg/km |  |
| Conductor Size AWG26/7 |  |  |  |  |  |  |  |  |
| 10 | 0.16 | 147 | 1.3 | 0.15 | 1.5 | 9.1 | 95 |  |
| 20 | 0.16 | 147 | 1.3 | 0.15 | 1.5 | 10.7 | 130 |  |
| 23 | 0.16 | 147 | 1.3 | 0.15 | 1.5 | 11.3 | 155 |  |
| 25 | 0.16 | 147 | 1.3 | 0.15 | 1.5 | 11.8 | 170 | 76130003 |
| 30 | 0.16 | 147 | 1.3 | 0.15 | 1.5 | 12.6 | 185 |  |
| 32 | 0.16 | 147 | 1.3 | 0.15 | 1.5 | 12.6 | 195 |  |
| 34 | 0.16 | 147 | 1.3 | 0.15 | 1.5 | 13.0 | 205 |  |
| 37 | 0.16 | 147 | 1.3 | 0.15 | 1.5 | 13.0 | 215 | 76130002 |
| 52 | 0.16 | 147 | 1.3 | 0.20 | 1.5 | 15.0 | 285 |  |
| 56 | 0.16 | 147 | 1.3 | 0.20 | 1.5 | 15.4 | 310 |  |